{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["Invulblad","Blad2","Blad3"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":1,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Invulblad","index":0,"n_rows":389,"n_cols":10,"rows_kept":389,"cut":false,"hidden":false,"merged":[[170,8,170,9]]}
[]
[]
[]
[null,null,null,null,null,null," "]
[null,null,"Periodieke Onderhoud"]
[null,null,"GAD/GAR toestel"]
[null,null,"Scope 1"]
[]
[]
["Rapportnummer",null,"PO118/4567BF226/1"]
["Aantal bladen",null,5]
[" ",null," "]
[]
["Project",null,"Naam",":","ABN Amro"]
[" ",null,"Adres",":","Plevierstraat 1"]
[null,null,"PC Woonplaats",":","1234AB Amsterdam"]
[null,null,"Telefoonnummer",":",201234567]
[null,null,"Contactpersoon",":","Dhr Alberts"]
[]
[]
["Opdrachtgever       ",null,"Naam",":","ABN Amro"]
[null,"  ","Adres",":","Plevierstraat 1"]
[null,"   ","PC Woonplaats",":","1234AB Amsterdam"]
[null,null,"Telefoonnummer",":",201234567]
[null,null,"Contactpersoon",":","Dhr Alberts"]
[null," ","Onderhoudsnummer",":",508822]
[]
["Onderhoud door    ",null,"Naam",":",1]
[null,"          ","Adres",":",1]
[null,null,"PC Woonplaats",":",1]
[null,null,"Technicus",":",1]
[null,"   ","Uitvoeringsdatum",":","1900-01-01"]
[null,null,"Installatie / toestel",":","Cv / Remeha gas 310"]
[null,"  ","Serienummer toestel",":","151458745875"]
[null,null,"Staat van onderhoud gehele installatie       :",":","test"]
["Scios installatiecode",null,null,":","AAA-111-BQ"]
[]
["EBI rapportage aanwezig op locatie",null,null,":","Ja, kopie"]
["Datum Eerste bijzondere inspectie",null,null,":","2001-01-01"]
["EBI uitgevoerd door firma /uitgevoerd door  ",null,null,":","Inspectiebedrijf / Klaas Jansma"]
["Basisverslag kenmerk",null,null,":","123ebi456"]
[]
[]
[]
[" "]
["Gerep/vervangen",null,"Onderhoudset plus pakkingen"]
["onderdelen"]
[]
[]
["Opmerkingen:",null,"Installatie ziet er netjes uit"]
[]
[]
[]
[]
[]
[]
[]
[]
["Evt. bovengenoemde punten dienen te worden hersteld."]
[]
["De technicus, bevoegd uitvoeren PO"]
[]
["Naam:  ","piet"]
[]
["Handtekening:"]
[]
[]
[]
[]
[]
["N.B. Dit rapport mag slechts in zijn geheel zonder enige toevoegingen of weglatingen geplubiceerd worden."]
["       onafhankelijk van de inhoud van dit rapport aanvaardt Schouten Techniek geen enkele aansprakelijkheid"]
["       ten aanzien van de installatie"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Algemene gegevens onderhoud"]
[]
["Toepassing installatie",null,null,"Cv"]
["Installatie geschikt voor",null,null,"Aardgas"]
["Valt onder SCIOS-Scope",null,null,1]
["Gasleveringsdruk",null,null,30,"mbar"]
[]
[]
[]
[]
["Meetapparatuur"]
[]
["Soort",null,"rookgasanalysemeter",null,"Fabrikaat",null,"Testo"]
["Type nr",null,1,null,"Serie nr",null,1]
["Kalibratie geldig tot",null,"1900-01-02"]
[]
["Soort",null,"gasdrukmeter",null,"Fabrikaat",null,"Euroindex"]
["Type nr",null,1,null,"Serie nr",null,1]
["Kalibratie geldig tot",null,"1900-01-02"]
[]
["Soort",null,"multimeter",null,"Fabrikaat",null,"Fluke"]
["Type-nr",null,1,null,"Serie nr",null,1]
["Kalibratie geldig tot",null,"1900-01-02"]
[]
[]
[]
[]
["HET DOEL VAN HET ONDERHOUD HOUDT IN:"]
[]
["-","Het reinigen van de installatie delen van de ketel en brander;"]
["-","Het op juiste wijze functioneren van de brander/ ketelcombinatie waarbij  "]
[null,"wordt gekeken naar zowel het stooktechnische- als de warmte- "]
[null,"economische werking van de installatie;  (rendement)"]
["-","Het controleren en zonodig reinigen van de ventilatie openingen van de stookruimte;"]
[" - ","De belastinginstellingen controleren overeenkomstig de technische gegevens van het toestel;"]
[" - ","Kwaliteit van onderhoud overeenkomstig de technische staat van de installatie c.q.basisverslag."]
[null,"gelet op de bedrijfszekerheid;"]
[" "," "]
[" "]
["Het onderhoud is volgens de certificaatieregeling en richtlijnen van de fabrikant uitgevoerd en hierbij "]
["rekening houdend met navolgende punten:"]
[]
["-","Veiligheid"]
["-","Bescherming van het milieu"]
["-","Beperking van het energie verbruik."]
[]
[]
["Gebruikte afkortingen en coderingen"]
[]
[null,"Actie:"]
[]
[null,"V","Vergrendeling",null,null,"A1","Afsluiter"]
[null,"HV","Harde vergrendeling",null,null,"F","Filter"]
[null,"ZV","Zachte vergrendeling",null,null,"K","Afsluitkraan"]
[null,"B","Blokkering",null,null,"DA","Drukafslag"]
[null,"O","Onderbreking",null,null,"DR1","Gasdrukregelaar"]
[" ","Sig","Signalering",null,null,"AV","Afblaasveiligheid"]
[null,null,null,null,null,"VA1","Veiligheidsafsluiter"]
[null,"PIN","Product Indentification Number",null,null,"VA2","Veiligheidsafsluiter"]
[null,"Scios","Stichting Certificatie Inspectie en Onderhoud Stookinstallatie",null,null,"MK1","Magneetklep"]
[null,"VPS","Valve Proving System",null,null,"MK2","Magneetklep"]
[null,null,null,null,null,"MB","Gasmultiblok"]
[null,"HB","Hoofdbrander",null,null,"HR1","Gashoeveelheidsregelaar"]
[null,"LTL","Laag-toeren-laag",null,null,"HR2","Luchthoeveelheidsregelaar"]
[null,"LTH","Laag-toeren-hoog",null,null,"LD","Minimum gasdrukbewaking"]
[null,"HTL","Hoog-toeren-laag",null,null,"LD1","Minimum gasdrukbewaking"]
[null,"HTH","Hoog-toeren-hoog",null,null,"LD2","Minimum luchtdrukbewaking"]
[null,"LT","Laag-toeren",null,null,"HD","Maximum gasdrukbewaking"]
[null,"HT","Hoog-toeren",null,null,"ES1","Startstand bewaking"]
[null,null,null,null,null,"ES2","Bewaking gesloten stand VA"]
[null,"bwv","Begin warmtevraag",null,null,"ES3","Bewaking ventilatiestand luchtklep"]
[null,"ewv","Einde warmtevraag",null,null,"M","Manometer"]
[null,"bvp","Begin ventilatieperiode",null,null,"GRB","Gasregelblok"]
[null,"ntb","Niet te bepalen"]
[null,"sec","Seconden"]
[null,"Δp","Delta P (drukverschil)"]
[]
[]
[]
[]
[]
[]
[]
[]
["STOOKPROEF GAS"]
[]
["Branderbelasting (stand van de regeling)",null,null,null,null,"Hoog","Laag","Halflast"]
["Toerental ventilator",null,null,null,"rpm",2000,1400,900]
["Druk voor DR1 (gas)",null,null,null,"mbar",100,100,100]
["Druk na DR1 (gas)",null,null,null,"mbar",30,30,30]
["Voordruk tijdens bedrijf bij de gasmeter",null,null,null,"mbar",100,100,100]
["Gashoeveelheid gasmeter",null,null,null,"m³",1.3,1.3,1.3]
["Totaal aantal gemeten seconden",null,null,null,"seconden",74,74,74]
["Gasverbruik m³s",null,null,null,"m³/h",22,44,14]
["Temperatuur gas",null,null,null,"ºC",12,12,12]
["Barometerstand",null,null,null,"mbar",1013,1013,1013]
["Belasting Hi",null,null,null,"kW",0,0,0]
["Aansteekbelasting hoofdbrander Hi",null,null,null,"kW",0,0,0]
["Belasting aansteekbrander",null,null,null,"kW",0,0,0]
["Luchtdruk tijdens ventileren ter plaatse van LD2",null,null,null,"mbar",0,0,0]
["Voordruk bedrijf bij de ketel",null,null,null,"mbar",29,29,29]
["Branderdruk / Kopdruk",null,null,null,"mbar",2.2999999999999998,2.2999999999999998,2.2999999999999998]
["Temperatuur rookgas",null,null,null,"ºC",58,58,58]
["Temperatuur verbrandingslucht",null,null,null,"ºC",20,20,20]
["O2",null,null,null,"vol.%",4.7,4.7,4.7]
["CO2",null,null,null,"vol.%",9.08,9.08,9.08]
["CO",null,null,null,"ppm",20,20,20]
["CO luchtvrij",null,null,null,"ppm",29,29,29]
["Medium druk",null,null,null,"bar",2.1,2.1,2.1]
["Medium temperatuur",null,null,null,"ºC",55,55,55]
["Signaal Vlamdetector",null,null,null,"µA",">10",">10",">10"]
["Vlam stabiel",null,null,null,"ja/nee","ja","ja","ja"]
["Schoorsteenverlies",null,null,null,"%",2.2999999999999998,2.2999999999999998,2.2999999999999998]
["Schoorsteenrendement Hi",null,null,null,"%",97.7,97.7,97.7]
["Vermogen o.b.v. schoorsteenverlies",null,null,null,"kW",0,0,0]
["Opgegeven vermogen installatie (N.V.)",null,null,null,"kW",0,0,0]
[]
["We zijn uitgegaan van navolgende "]
["1m³s","Hi 30,00 Mj","(st)(Gronings gas)"]
[null,"Hs 33,34 Mj","(st)(Gronings gas)"]
[]
["Drukschakelaars:",null,"LD2 ventileren","LD2L","LD2H","LD1","HD","Hdstart"]
["Gemeten druk mbar",null,5.8,0,0,0,0,0]
["Schakeldruk mbar",null,5,0,0,0,0,0]
["Soort ingreep",null,"blokkerend",0,0,0,0,0]
[" "]
[" "]
["Opmerkingen:",null,111]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Aandachtspunten  onderhoud",null,null,null,null,"status",null,"Opmerking"]
[null,null,null,null,null,"g/f/nvt"]
["1e warmtewisselaar",null,"Warmtewisselaar","Waterlekkage",null,"g "]
[null,null,null,"Corrosie",null,"g "]
[null,null,null,"Vervuiling",null,"g"]
[" ",null,"Retarders","Conditie",null,"g"]
[null,null,null,"Reparatie",null,"g","Bij te hoge vuurhaarddruk en rookgastemp."]
[null,null,null,"Reinigen",null,"g","mits in contract"]
[null,null,"Keerschotten / -kasten","Aanwezig",null,"g"]
[null,null,null,"Conditie",null,"g"]
[null,null,null,"Reparatie",null,"g"]
[null,null,null,"Reinigen",null,"g"]
[null,null,"Bekleding (ook in sommige wandketels)","Aanwezig",null,"g","Vuurvaste isolatie, bemetseling en stenen"]
[null,null,null,"Conditie",null,"f"]
[null,null,null,"Reparatie",null,"f"]
[null,null,"Isolatie binnen de mantel","Aanwezig",null,"f"]
[null,null,null,"Conditie",null,"n"," "]
[null,null,null,"Reparatie",null,"nvt"]
[null,null,"Verbrandingsgaslekkage","Intern en extern",null,"nvt"]
[null,null,"Rookgasverzamelkast","Corrosie",null,"g"]
[null,null,"Veiligheidsklep volgens EBI","Tijdig vervangen (10 jaar) of testen",null,"g"]
[null,null,null,"Werking",null,"g"]
[null,null,null,"Geen lekkage",null,"g"]
[null,null,"Condensafvoer","Reinigen sifon",null,"g"]
[null,null,"Mediumregel- en ","Conditie",null,"g","Functioneel testen en testen op schakel-"]
[null,null,"beveiligingsorganen","Instellingen",null,"f","waarde tenzij de fabrikant van het stook-"]
[null,null,null,"Werking",null,"f","toestel anders aangeeft"]
[]
[]
["2e warmtewisselaar",null,"Veiligheidsklep volgens EBI","Tijdig vervangen (10 jaar) of testen",null,"f"]
[null,null,null,"Werking",null,"f"]
[null,null,null,"Geen lekkage",null,"f"]
[null,null,"Condensafvoer","Reinigen sifon",null,"f"]
[null,null,"Mediumregel- en ","Conditie",null,"f","Functioneel testen en testen op schakel-"]
[null,null,"beveiligingsorganen","Instellingen",null,"f","waarde tenzij de fabrikant van het stook-"]
[null,null,null,"Werking",null,"f","toestel anders aangeeft"]
[]
[]
["Branderautomaat",null,"BMS","Juiste BMS volgens opgave fabrikant",null,"f"]
[null,null,null,"Conditie",null,"f"]
[null,null,"Totale sluittijd","Gemeten in seconden",null,"f"]
[null,null,"Vlambeveiliging","Reinigen",null,"g"]
[null,null,null,"Controle",null,"f"]
[null,null,null,"Reparatie",null,"f"]
[null,null,"Ontsteekelektrode","Conditie",null,"f"]
[null,null,null,"Functioneren",null,"f"]
[null,null,null,"Reparatie",null,"f"]
[]
[]
["Brandstof toevoer vanaf",null,"Handbediende afsluiter ","Conditie",null,"g"]
["afsluiter A1 (olie of gas)",null,"(gasA1-olie)","Gangbaarheid",null,"g"]
[null,null,null,"Afsluitbaarheid",null,"g"]
[null,null,"Brandstoftoevoer (gasA1-olie)","Conditie",null,"g"]
[null,null,"Filter (gas-olie)","Aanwezig en geschikt",null,"g"]
[null,null,null,"Reinigen",null,"g"]
[null,null,"Lektest apparatuur (gas)","Wijze van testen:",null,"g"]
[null,null,null,"Conditie",null,"g"]
[null,null,null,"Functioneren",null,"g"]
[null,null,"Gas-/ oliedrukschakelaars","Afstelling",null,"g","Test tijdens bedrijf"]
[null,null,null,"Funtioneren volgens basisverslag",null,"g","Test, droog/tijdens spoelen"]
[null,null,"Gas-/ oliehoeveelheidsregelaar","Juiste inregeling klep",null,"g","Stookproef/drukmeting"]
[null,null,null,"juiste inregeling drukregelaar",null,"g"]
[null,null,null,"Conditie",null,"g"]
[null,null,null,"Functioneren",null,"g"]
[null,null,"Oliepomp","Juiste inregeling",null,"g","Via stookproef"]
[null,null,null,"Conditie",null,"g"]
[null,null,null,"Functioneren",null,"g"]
[null,null,"Eindschakelaars (gas/ olie)","Afstelling",null,"g"]
[null,null,null,"Conditie",null,"g"]
[null,null,"Beveiliging afsluiters (gas/ olie)","Werking",null,"g"]
[null,null,null,"Inwendige lekkage",null,"g"]
[null,null,null,"Conditie",null,"g"]
[null,null,"Adem- en afblaasleidingen","Conditie",null,"g"]
[null,null,null,"Functioneren",null,"g"]
[null,null,"Flexibele verbinding","Conditie",null,"g"]
[null,null,"Menger/nuldrukregelaar","Juiste inregeling",null,"g","Via stook- / belastingproef"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Aandachtspunten  onderhoud (vervolg)",null,null,null,null,"status",null,"Opmerking"]
[null,null,null,null,null,"g/f/nvt"]
["Rookgas-",null,"Rookgaskleppen","Functioneren",null,"f"]
["afvoer",null,null,"Conditie",null,"f"]
[null,null,null,"Reinigen",null,"f"]
[null,null,null,"Functioneren (afstelling eindschakelaar)",null,"f"]
[null,null,null,"Conditie eindschakelaar",null,"f"]
[null,null,"Trekregelaar/-regeling","Functioneren",null,"f"]
[null,null,null,"Conditie",null,"f"]
[null,null,null,"Reinigen",null,"f"]
[null,null,"Afvoerkanaal /-leiding","Conditie (constructie en dichtheid)",null,"g"]
[null,null,"Condensafvoer","Vervuiling",null,"f"]
[null,null,null,"Reinigen",null,"f"]
[null,null,"Afvoerbeveiliging","Werking",null,"f"]
[null,null,"Afvoerkap","Conditie",null,"f"]
[null,null,null,"Reinigen",null,"f"]
[null,null,null,"Functioneren",null,"f"]
[null,null,"Transportbewaking rookgasafvoer","Conditie",null,"f"]
[null,null,null,"Reinigen",null,"f"]
[null,null,null,"Functioneren",null,"g"]
[]
[]
["Opstelling toestel",null,"Stookruimte/opstellingsruimte/","Schoon",null,"g"]
[null,null,"opstelplaats algemeen","Geen opslagruimte",null,"g"]
[null,null,null,"Brandblusser aanwezig",null,"g"]
[null,null,null,"Vluchtweg",null,"g"]
[null,null,"Luchttoevoer","Netto doorlaat",null,"g","EBI: Kruiskap voorschrift?"]
[null,null,null,"Schermplaat",null,"g","Afstand"]
[null,null,null,"Ventilatie luchttoevoerleiding",null,"g","Netto doorlaat, conditie"]
[null,null,null,"Controle vervuiling",null,"g"]
[null,null,null,"Reinigen",null,"g"]
[null,null,"Ventilatieafvoer","Netto doorlaat",null,"g","Trekkende kap aanwezig?"]
[null,null,null,"Controle vervuiling",null,"g"]
[null,null,null,"Reinigen",null,"g"]
[null,null,"Mechanische luchttoevoer/","Controle vervuiling",null,"g"]
[null,null,"mechanische ventilatie","Reinigen",null,"g"]
[null,null,"Transportbeveiliging mechanische","Conditie",null,"g"]
[null,null,"Luchttoevoer of -ventilatie","Werking",null,"g"]
[null,null,"Noodschakelaar","Aanwezig en werking",null,"g"]
[null,null,"Vuilwaterpomp","Werking/ smering",null,"g","Vaste- of dompelpomp bij vloer onder "]
[null,null,null,null,null,"f","maaiveld"]
[null,null,"Verlichting","Voldoende",null,"g"]
[null,null,"Ruimtetemperatuur regeling","Conditie",null,"g"]
[null,null,"en -bewaking"]
[]
[]
["Stookproef",null,"Vlamstabiliteit",null,"beoordelen","test"]
[" ",null," ",null," "]
[null,null,null,null," "]
["Opmerkingen algemeen:",null,"geen",null," ","   "]
[]
[]
[]
[null,null," ",null," "," "]
[]
[]
[null,null,null,null,null,"g=goed     ","f=fout","nvt=niet van toepassing",null," "]

{"sheet":"Blad2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[[2,4,2,6]]}

{"sheet":"Blad3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}